## VSD Template
AIR BLOWER PACKAGE DATA SHEET
Positive Displacement Variable Speed Blower
MODEL DATA - Standard Conditions (US Units)
| 1 | Manufacturer: | Atlas Copco |  |  |  | Date: | 2024-10-31
| 2 | Model Number: | ZL 4 VSD 75kW-G
3
[8 empty] | VALUE | UNITS
| 4 | Capacity (FAD) at Rated Design Pressure | [5 empty] | 1298 | cfm
| 5 | Rated Design Pressure - p2 | [5 empty] | 10 | psig
| 6 | Drive Motor Nominal Rating | [5 empty] | 100 | hp
| 7 | Blower Speed at Design Capacity | [5 empty] | 3694 | rpm
| 8 | Maximum Operating Pressured | [5 empty] | 14.5 | psig
| 9 | Performance Tableª
|  | Discharge Pressure p2 (psig)ᵇ |  |  | Delivered Air Flow - FAD (cfm)
[5 empty] | MIN FAD | FADᶜ | FADᶜ | FADᶜ | 100% FAD
|  | 12 psig |  | FADf | 591.45 | 761.57 | 931.7 | 1101.82 | 1271.94
|  |  |  | Spec. Powere | 6.61 | 6.23 | 6.08 | 6.06 | 6.13
|  |  |  | Blower Speed (rpm) | 1907.01 | 2338.82 | 2782.34 | 3234.82 | 3693.97
|  | 10 psig |  | FADf | 609.42 | 781.54 | 953.66 | 1125.78 | 1297.9
|  |  |  | Spec. Powere | 5.49 | 5.18 | 5.05 | 5.03 | 5.06
|  |  |  | Blower Speed (rpm) | 1907.02 | 2341.05 | 2784.64 | 3236.12 | 3693.97
|  | 8 psig |  | FADf | 629.28 | 803.04 | 976.81 | 1150.57 | 1324.33
|  |  |  | Spec. Powere | 4.43 | 4.2 | 4.11 | 4.09 | 4.12
|  |  |  | Blower Speed (rpm) | 1907.02 | 2342.96 | 2786.75 | 3237.4 | 3693.97
Notes:
a. Based on reference inlet conditions
of pamb=14.7 psia, Tamb=68°F,
RH=36%
b. Discharge pressure in -2 psig
increments
c. Intermediate points at equal
spacing between 100% and Min.
Flow
d. Data not shown
e. Specific power (kW /100 cfm)
tolerance of +/- tolerance given by
Table 2 in BL 300 unless "No Negative
Tolerance" box is checked
f. Delivered air flow +/- tolerance
given by Table 2 in BL 300 unless "No
Negative Tolerance" box is checked
Member
BL 082 (US Units)
07/24 R8 |  | This form was developed by the Compressed Air and Gas Institute for the use of its members. CAGI has not independently verified the reported data.
Table 2 from BL 300: