## VSD Template
AIR BLOWER PACKAGE DATA SHEET
Positive Displacement Variable Speed Blower
MODEL DATA - Standard Conditions (US Units)
| 1 | Manufacturer: | Atlas Copco |  |  |  | Date: | 2024-10-31
| 2 | Model Number: | ZS 4 VSD 75kW-L
3
[8 empty] | VALUE | UNITS
| 4 | Capacity (FAD) at Rated Design Pressure | [5 empty] | 1878 | cfm
| 5 | Rated Design Pressure - p2 | [5 empty] | 10 | psig
| 6 | Drive Motor Nominal Rating | [5 empty] | 100 | hp
| 7 | Blower Speed at Design Capacity | [5 empty] | 3573 | rpm
| 8 | Maximum Operating Pressured | [5 empty] | 17.4 | psig
| 9 | Performance Tableª
|  | Discharge Pressure p2 (psig)ᵇ |  |  | Delivered Air Flow - FAD (cfm)
[5 empty] | MIN FAD | FADᶜ | FADᶜ | FADᶜ | 100% FAD
|  | 12 psig |  | FADf | 446.96 | 798.18 | 1149.39 | 1500.61 | 1851.83
|  |  |  | Spec. Powere | 4.93 | 4.37 | 4.32 | 4.43 | 4.65
|  |  |  | Blower Speed (rpm) | 1000.01 | 1614.06 | 2238.4 | 2875.57 | 3528.21
|  | 10 psig |  | FADf | 451 | 808 | 1165 | 1522 | 1878
|  |  |  | Spec. Powere | 4.29 | 3.79 | 3.77 | 3.89 | 4.11
|  |  |  | Blower Speed (rpm) | 1000.01 | 1624.49 | 2259.68 | 2908.24 | 3572.96
|  | 8 psig |  | FADf | 455.77 | 812.18 | 1168.59 | 1525 | 1881.41
|  |  |  | Spec. Powere | 3.71 | 3.23 | 3.22 | 3.36 | 3.55
|  |  |  | Blower Speed (rpm) | 1000.01 | 1624.46 | 2259.65 | 2908.22 | 3572.96
Notes:
a. Based on reference inlet conditions
of pamb=14.7 psia, Tamb=68°F,
RH=36%
b. Discharge pressure in -2 psig
increments
c. Intermediate points at equal
spacing between 100% and Min.
Flow
d. Data not shown
e. Specific power (kW /100 cfm)
tolerance of +/- tolerance given by
Table 2 in BL 300 unless "No Negative
Tolerance" box is checked
f. Delivered air flow +/- tolerance
given by Table 2 in BL 300 unless "No
Negative Tolerance" box is checked
Member
BL 082 (US Units)
07/24 R8 |  | This form was developed by the Compressed Air and Gas Institute for the use of its members. CAGI has not independently verified the reported data.
Table 2 from BL 300: